## status
no | list parameter | status |  |  |  | NMS
|  | 00H | 01H | 02H | F0H
1 | cell 1 voltage | normal | lower limit | upper limit | other error | √
2 | cell 2 voltage | normal | lower limit | upper limit | other error | √
3 | cell 3 voltage | normal | lower limit | upper limit | other error | √
4 | cell 4 voltage | normal | lower limit | upper limit | other error | √
5 | cell 5 voltage | normal | lower limit | upper limit | other error | √
6 | cell 6 voltage | normal | lower limit | upper limit | other error | √
7 | cell 7 voltage | normal | lower limit | upper limit | other error | √
8 | cell 8 voltage | normal | lower limit | upper limit | other error | √
9 | cell 9 voltage | normal | lower limit | upper limit | other error | √
10 | cell 10 voltage | normal | lower limit | upper limit | other error | √
11 | cell 11 voltage | normal | lower limit | upper limit | other error | √
12 | cell 12 voltage | normal | lower limit | upper limit | other error | √
13 | cell 13 voltage | normal | lower limit | upper limit | other error | √
14 | cell 14 voltage | normal | lower limit | upper limit | other error | √
15 | cell 15 voltage | normal | lower limit | upper limit | other error | √
16 | cell 16 voltage | normal | lower limit | upper limit | other error | √
17 | cell temperature 1 | normal | lower limit | upper limit | other error | √
18 | cell temperature 2 | normal | lower limit | upper limit | other error | √
19 | cell temperature 3 | normal | lower limit | upper limit | other error | √
20 | cell temperature 4 | normal | lower limit | upper limit | other error | √
21 | mosfet temperature 5 | normal | lower limit | upper limit | other error | √
22 | enviroment temperature 6 | normal | lower limit | upper limit | other error | √
23 | pack charging current | normal | lower limit | upper limit | other error | √
24 | pack voltage | normal | lower limit | upper limit | other error | √
25 | pack discharging | normal | lower limit | upper limit | other error | √
26 | fully | no | yes |  |  | √
27 | current limiting circuit | off | on |  |  | √
28 | charging mosfet | off | on |  |  | √
29 | discharging mosfet | off | on |  |  | √
30 | power supply | off | on |  |  | √
31 | ac in | no | yes |  |  | x
32 | state of heater | off | on |  |  | √
33 | buzzer warning function | disable | enable |  |  | √
34 | current limit control | 10A | 5A |  |  | x
35 | current limit function | disable | enable |  |  | √
36 | led warning function | disable | enable |  |  | √
37 | cell 1 balancing | off | on |  |  | x
38 | cell 2 balancing | off | on |  |  | x
39 | cell 3 balancing | off | on |  |  | x
40 | cell 4 balancing | off | on |  |  | x
41 | cell 5 balancing | off | on |  |  | x
42 | cell 6 balancing | off | on |  |  | x
43 | cell 7 balancing | off | on |  |  | x
44 | cell 8 balancing | off | on |  |  | x
45 | cell 9 balancing | off | on |  |  | x
46 | cell 10 balancing | off | on |  |  | x
47 | cell 11 balancing | off | on |  |  | x
48 | cell 12 balancing | off | on |  |  | x
49 | cell 13 balancing | off | on |  |  | x
50 | cell 14 balancing | off | on |  |  | x
51 | cell 15 balancing | off | on |  |  | x
52 | cell 16 balancing | off | on |  |  | x

## alarm
No | list parameter | status alarm |  | NMS
|  | 00H | 01H
1 | cell over voltage protect | normal | active | √
2 | cell under voltage protect | normal | active | √
3 | pack over voltage protect | normal | active | √
4 | pack under voltage protect | normal | active | √
5 | charging over current protect | normal | active | √
6 | discharging over current protect | normal | active | √
7 | short circuit protect | normal | active | √
8 | charging over temperature protect | normal | active | √
9 | discharging over temperature protect | normal | active | √
10 | charging under temperature protect | normal | active | x
11 | discharging under temperature protect | normal | active | x
12 | mosfet over temperature protect | normal | active | √
13 | environment over temperature protect | normal | active | √
14 | environment under temperature protect | normal | active | x
15 | discharging mosfet fault | normal | active | √
16 | charging mosfet fault | normal | active | √
17 | temperature ntc fault | normal | active | √
18 | battery voltage fault | normal | active | x
19 | sampling fault | normal | active | x
20 | pack over voltage warning | normal | active | √
21 | pack under voltage warning | normal | active | √
22 | cell over voltage warning | normal | active | √
23 | cell under voltage warning | normal | active | √
24 | charging over current warning | normal | active | √
25 | discharging over current warning | normal | active | √
26 | charging over temperature warning | normal | active | √
27 | discharging over temperature warning | normal | active | √
28 | charging under temperature warning | normal | active | x
29 | discharging under temperature warning | normal | active | x
30 | environment over temperature warning | normal | active | √
31 | environment under temperature warning | normal | active | x
32 | mos over temperature warning | normal | active | √
33 | soc low warning | normal | active | √

## measurement
no | list parameter | value | unit | NMS
1 | cell 1 voltage | 0 | V | √
2 | cell 2 voltage | 0 | V | √
3 | cell 3 voltage | 0 | V | √
4 | cell 4 voltage | 0 | V | √
5 | cell 5 voltage | 0 | V | √
6 | cell 6 voltage | 0 | V | √
7 | cell 7 voltage | 0 | V | √
8 | cell 8 voltage | 0 | V | √
9 | cell 9 voltage | 0 | V | √
10 | cell 10 voltage | 0 | V | √
11 | cell 11 voltage | 0 | V | √
12 | cell 12 voltage | 0 | V | √
13 | cell 13 voltage | 0 | V | √
14 | cell 14 voltage | 0 | V | √
15 | cell 15 voltage | 0 | V | √
16 | cell 16 voltage | 0 | V | √
17 | cell temperature 1 | 00 | °C | √
18 | cell temperature 2 | 00 | °C | √
19 | cell temperature 3 | 00 | °C | √
20 | cell temperature 4 | 00 | °C | √
21 | mosfet temperature | 00 | °C | √
22 | enviroment temperature | 00 | °C | √
23 | pack charging current | 00.00 | A | √
24 | pack voltage | 00.00 | V | √
25 | remain capacity | 00 | AH | √
26 | full capacity | 00 | AH | √
27 | discharge charger cycle count | 0000 | cycle | √
28 | design capacity | 000 | AH | √

## Set
no | code | item parameter | valeu parameter | threshold | default | interval | unit | NMS
1 | 44 30 | enable (ceklis) | √ atau × |  |  |  |  | x
2 |  | cell over charge voltage alarm (V) | =x/1000 V | 3.30-3.90 | 3.6 | 0.01 | V | x
3 |  | cell over charge voltage protection (V) | =x/1000 V | 3.30-3.90 | 3.7 | 0.01 | V | x
4 |  | cell over charge protection release (V) | =x/1000 V | 3.30-3.90 | 3.38 | 0.01 | V | x
5 |  | cell over charge protection delay time (mS) | =x*100 mS | 500-5000 | 1000 | 100 | mS | x
6 | 44 34 | enable (ceklis) | √ atau × |  |  |  |  | √
7 |  | pack over charge voltage alarm (V) | =x/1000 V | 25.0-59.9 | 57.6 | 0.1 | V | √
8 |  | pack over charge voltage protection (V) | =x/1000 V | 25.0-59.9 | 58.4 | 0.1 | V | √
9 |  | pack over charge protection release (V) | =x/1000 V | 25.0-59.9 | 54 | 0.1 | V | √
10 |  | pack over charge protection delay time (mS) | =x*100 mS | 500-5000 | 1000 | 100 | mS | √
11 | 44 32 | enable (ceklis) | √ atau × |  |  |  |  | x
12 |  | cell under discharge voltage alarm (V) | =x/1000 V | 2.00-3.50 | 2.8 | 0.01 | V | x
13 |  | cell under discharge voltage protection (V) | =x/1000 V | 2.00-3.50 | 2.5 | 0.01 | V | x
14 |  | cell under discharge protection release (V) | =x/1000 V | 2.00-3.50 | 3 | 0.01 | V | x
15 |  | cell under discharge protection delay time (mS) | =x*100 mS | 500-5000 | 1000 | 100 | mS | x
16 | 44 36 | enable (ceklis) | √ atau × |  |  |  |  | √
17 |  | pack under discharge voltage alarm (V) | =x/1000 V | 18.0-54.9 | 43.2 | 0.1 | V | √
18 |  | pack under discharge voltage protection (V) | =x/1000 V | 18.0-54.9 | 40 | 0.1 | V | √
19 |  | pack under discharge protection release (V) | =x/1000 V | 18.0-54.9 | 48 | 0.1 | V | √
20 |  | pack under discharge protection delay time (mS) | =x*100 mS | 500-5000 | 1000 | 100 | mS | √
21 | 44 38 | enable (ceklis) | √ atau × |  |  |  |  | √
22 |  | charge over current alarm (A) | A | 1-150 | 100 | 1 | A | √
23 |  | charge over current protection (A) | A | 1-150 | 105 | 1 | A | √
24 |  | charge over current protection delay time(A) | =x*100 mS | 500-5000 | 1000 | 100 | mS | √
25 | 44 41 | enable (ceklis) | √ atau × |  |  |  |  | √
26 |  | discharge over current alarm (A) | A | 1-150 | 100 | 1 | A | √
27 |  | discharge over current protection (A) | A | 1-150 | 105 | 1 | A | √
28 |  | discharge over current protection delay time(A) | =x*100 mS | 500-5000 | 1000 | 100 | mS | √
29 | 45 32 | enable (ceklis) | √ atau × |  |  |  |  | √
30 |  | discharge over current_2 protection (A) | A | 1-200 | 150 | 1 | A | √
31 |  | discharge over current_2 protection delay time(mS) | =x*25 mS | 50-2000 | 50 | 50 | mS | √
32 | 45 34 | short circuit protection delay time(uS) | =x*25 uS | 100-500 | 300 | 50 | uS | √
33 | 42 35 | cell balance threshold (V) | =x/1000 V | 3.00-4.00 | 3.4 | 0.01 | V | x
34 |  | delta Vcell (mV) | mV | 5-500 | 30 | 5 | mV | x
35 | 41 38 | cell sleep voltage (V) | =x/1000 V | 2.50-4.00 | 3.1 | 0.01 | V | x
36 |  | delay time (min) | min | 1-120 | 1 | 1 | Minute | x
37 | 41 45 | fully charge voltage (V) | =x/1000 V | 25.0-59.9 | 56 | 0.01 | V | x
38 |  | fully charge cutoff current (mAH) | mAH | 300-2000 | 500 | 100 | mA | x
39 |  | SOC low alarm (%) | % | 0-100 | 30 | 1 | % | x
40 | 44 43 | enable (ceklis) | √ atau × |  |  |  |  | √
41 |  | charge over temperature alarm (deg C) | =(x-2739)/10 °C | 20-100 | 50 | 1 | °C | √
42 |  | charge over temperature protection (deg C) | =(x-2739)/10 °C | 20-100 | 55 | 1 | °C | √
43 |  | charge over temperature protection release (deg C) | =(x-2739)/10 °C | 20-100 | 50 | 1 | °C | √
44 |  | discharge over temperature alarm (deg C) | =(x-2739)/10 °C | 20-100 | 55 | 1 | °C | √
45 |  | discharge over temperature protection (deg C) | =(x-2739)/10 °C | 20-100 | 60 | 1 | °C | √
46 |  | charge over temperature protection release (deg) | =(x-2739)/10 °C | 20-100 | 55 | 1 | °C | √
47 | 44 45 | enable (ceklis) | √ atau × |  |  |  |  | √
48 |  | charge under temperature alarm (deg C) | =(x-2739)/10 °C | -35-30 | 0 | 1 | °C | √
49 |  | charge under temperature protection (deg C) | =(x-2739)/10 °C | -35-30 | -5 | 1 | °C | √
50 |  | charge under temperature protection release(deg C) | =(x-2739)/10 °C | -35-30 | 0 | 1 | °C | √
51 |  | discharge under temperature alarm (deg C) | =(x-2739)/10 °C | -35-30 | -20 | 1 | °C | √
52 |  | discharge under temperature protection (deg C) | =(x-2739)/10 °C | -35-30 | -25 | 1 | °C | √
53 |  | discharge under temperature protection release(deg C) | =(x-2739)/10 °C | -35-30 | -20 | 1 | °C | √
54 | 45 30 | enable (ceklis) | √ atau × |  |  |  |  | x
55 |  | mosfet over temperature alarm (deg C) | =(x-2739)/10 °C | 30-120 | 100 | 1 | °C | x
56 |  | mosfet over temperature protection (deg C) | =(x-2739)/10 °C | 30-120 | 105 | 1 | °C | x
57 |  | mosfet over temperature protection release (deg C) | =(x-2739)/10 °C | 30-120 | 95 | 1 | °C | x
58 | 45 36 | enable (ceklis) | √ atau × |  |  |  |  | x
59 |  | environment under temperature alarm (deg C) | =(x-2739)/10 °C | -35-30 | -20 | 1 | °C | x
60 |  | environment under temperature protection (deg C) | =(x-2739)/10 °C | -35-30 | -25 | 1 | °C | x
61 |  | environment under temperature protection release(deg C) | =(x-2739)/10 °C | -35-30 | -20 | 1 | °C | x
62 |  | environment over temperature alarm (deg C) | =(x-2739)/10 °C | -35-30 | 65 | 1 | °C | x
63 |  | environment over temperature protection (deg C) | =(x-2739)/10 °C | -35-30 | 70 | 1 | °C | x
64 |  | environment over temperature protection release(deg C) | =(x-2739)/10 °C | -35-30 | 65 | 1 | °C | x